## Summary
SCHEDULE OF ITEM AND BILL OF QUANTITIES : CUSTOM MADE JACKET FOR DEVINE MERCY HOSPITAL ATM BOOTH
SL | DESCRIPTION | AMOUNT
A | CIVIL WORKS | 0
B | PAINT WORKS | 0
C | ELECTRICAL WORKS | 0
D | NETWORKING WORKS | 0
E | ACP WORKS WITH FRAME, DOORS, PARTITIONS | 0
| TOTAL | 0

## BOQ
SCHEDULE OF ITEM AND BILL OF QUANTITIES : CUSTOM MADE JACKET FOR DEVINE MERCY HOSPITAL ATM BOOTH
SL | ITEMS | UOM | QTY | RATE | AMOUNT
A. CIVIL WORKS
1 | DISMANTLING , CLEANING & SITE PREPARATION [All necessary dismantling to complete the project] | JOB | 1 |  | 0
Sub Total = |  |  |  |  | 0
B. PAINT WORKS
1 | PLASTIC PAINT Plastic painting of ‘Berger’ brand of approved color to wall minimum 3 coats with lime putty work, cleaning, sand papering the surfaces in/c. necessary scaffolding etc. complete in all respect as per direction of Architect/ Authority. | SFT | 200 |  | 0
2 | ENAMEL PAINT Synthetic Enamel paint of ‘Berger’ brand of approved color to wall, ceiling, wooden surfaces, iron grills, shutters etc. minimum 2 coats over a coat of priming including cleaning, finishing and polishing with sand paper and necessary scaffolding etc. complete in all respect as per direction of Architect/Authority. | SFT | 100 |  | 0
Sub Total = |  |  |  |  | 0
C. ELECTRICAL WORKS
1 | Concealed/exposed conduit wiring for following light points including louver shade/PL shade & light/Tube light & its components with looping at the gang (1G/2G/3G/4G as required) switch including grooving/wall cutting, circuit wiring (circuit breaker to Switch) with BYA 1C-2X2.5 Sq.mm, BYA 1C-2X1.5 sq. mm (switch to light) for light wiring & BYA1CX1.0 sq. mm green ECC through PVC conduit of good quality of minimum 3/4" dia complete with all fixing materials following the provided design. Cable brand: BRB/Paradise GANG SWITCHES brand: Legrand/MK brand Light brand :EnegryPac/Philips/Transtec Light Type : LED (13 W)
1.1 | 1 light though 1 switch | NOS | 2 |  | 0
1.2 | DP switch for signage | NOS | 1 |  | 0
2 | Concealed conduit wiring for following points through looping at the socket/outlet of 5A/13A/15A including grooving/wall cutting, circuit wiring with BYA 1C-2X2.5 Sq.mm & BYA 1CX1.5 sq. mm green ECC through PVC conduit of good quality of minimum 3/4" dia complete with all fixing materials following the provided design. Cable brand: BRB/Paradise SOCKET brand: Legrand/MK brand |  |  |  | 0
2.1 | Socket point |  |  |  | 0
2.2 | 2nos - 3pin & 1nos -2pin through 1 circuit | NOS | 2 |  | 0
2.3 | 2nos - 3pin & 1nos -2pin through 1 plug (UPS output to ATM) | NOS | 2 |  | 0
3 | CABLES WORKS: Supply and installation of following cables through required size PVC pipe with all consumable materials as per design, drawing and direction of Authority. Brand : BRB/Paradise |  |  |  | 0
3.1 | 1CX 6 rm BYA | RFT | 200 |  | 0
3.2 | 2.5 mm2 [Green] | RFT | 100 |  | 0
4 | MCCB/MCB: Supply and installation of following SP (240V grade) TP (500 V grade) MCB/MCCB in pre installed distribution board in/c connection with cable, cable socket, nut bolts, PIB tape etc. complete in respect providing necessary consumable in/c testing & commissioning as per design, drawing and direction of Authority. brand : Legrand/ABB MCCB/MCB’s brand: Legrand/ABB |  |  |  | 0
4.1 | 10 A to 40 A SP MCB-6 kA | NOS | 4 |  | 0
4.2 | 50 A to 63 A TP MCB-6 kA | NOS | 1 |  | 0
5 | DISTRIBUTION BOARD: Supplying and installation of distribution board [At least 2’ - 0” W x 3’ - 0” H, 6 sft] of required size made by 16 SWG B.P. sheet metal enclosed with double cover powder coated painted on outside and enamel paint on inside on rust proof prime coat with hinged front door with handle, lock & key arrangement for concealed/half concealed mounted board having knock out for conduit entry and exit for 415/230V TPN/SPN operations. The board shall have solid three phase, neutral and earth copper bus bar. MCCB/MCB’s are to be so arranged as to keep the knobs projected over the inside ebonite cover. There should be provision for fixing Air-Cooler circuit breakers and emergency circuit breakers as per requirement. The work shall be complete in all respect providing necessary consumable in/c testing & commissioning, as per design, drawing and direction of Architect/ Authority. Note: 1. Layout design of Distribution Board as suggested by Energypack Ltd. must be approved from the Consultant / Authority by the contractor before execution.
5.1 | SDB/ESDB for ATM (Customised)-vermin proff, using steel sheet thickness-20 SWG. Bus bar should be insulated by acrylic/PVC cover for safety. | NOS | 1 |  | 0
6 | EARTHLING SYSTEM: Supplying and installation of 100’-0” depth 1½” dia G.I. pipe earth electrode by tube well sinking method including supply of 2 SWG HDBC earthling lead from the bottom of earth electrode to the earthling bar of distribution board. Making an earth inspection pit of size 20” x 20” x 18” inside clear. Bottom of pit shall be 3” thick C.C. work and four side wall shall be 5” thick brick wall with ½” plastering and 3” thick R.C.C. cover slab. The top end of the electrode shall be 3” above from the bottom C.C. work. Complete in all respect in/c testing & commissioning, as per design, drawing and direction of Architect/ Authority. Note: 1. Voltage between neutral and earth [Inductive voltage] must be less than 2 volt. 2.The total arrangement must be theft proof as per site condition. | NOS | 1
Sub Total = |  |  |  |  | 0
D. IT & NETWORKING WORKS
1 | NEW NET CONNECTION : PVC Conduting, Data Phase Plate Single or Double, approved Brand Cat6 data cable, and labor charges for punching , dressing etc complete in all respect as per design, drawing and direction of Architect/Authority. Brand-Panduit/Systemax/AMP. | NOS | 3 |  | 0
Sub Total = |  |  |  |  | 0
E. ACP & PARTITIONS
1 | MS FRAME PARTITION: Supplying, fitting and fixing ms frame made of 2" x 2" x 5mm ms box fixed with royal bolt with all necessary hardwires etc. complete in all respect as per design, drawing and direction of Architect/Authority. | JOB | 1 |  | 0
2 | ALUMINUM COMPOSITE PANELING Supplying, fitting & fixing foreign made aluminum composite panel [Alcoban/Alcopla Brand] consisting to two thin [0.4mm] aluminum alloy sheets sandwich with them plastic composite core having total thickness 4 mm of approved color, panels fixed on aluminum structural sections, complete in all respect in/c necessary hardwires, sealant etc. in/c required scaffoldings etc. complete in all respect as per design, drawing and direction of Architect/Authority. | SFT | 395 |  | 0
3 | ALUMINUM LOUVER Supplying, fitting and fixing of aluminum louver screen to house outdoor AC units made of 4” section colored anodized / powder coated aluminum louver sections with all foreign made hardwires, sealant etc. in/c required scaffoldings etc. complete in all respect as per design, drawing and direction of Architect/Authority. | SFT | 10 |  | 0
4 | CHEQUE WRITING TABLE Supply & Installation as BBL Standard | NOS | 1
5 | SHELF FOR MONITOR (2'-0" X 1'-6") Inside the ACP frame | NOS | 1 |  | 0
6 | DOOR CONCEALED LOCK & HANDLE FOR AC FRAME DOOR | JOB | 1 |  | 0
Sub Total = |  |  |  |  | 0
TOTAL = |  |  |  |  | 0